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	Project Data

	Customer Company
	
	Offer Number
	

	Project Name
	
	Offer Date
	

	Unit Project Code
	
	
	



Product Specifications

	RTER035
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FOUR RTER-Rotor Type Heat Recovery Unit is used in restaurants, stores, historical buildings, offices where fresh air is needed. Designed to take charge of the air of fresh air. It works with indoor air conditioning devices. The exhaust air absorbed from the interior environment is transferred to the external
environment after the heat transfer with the fresh air thanks to the hygroscopic energy recovery rotor. With the automatic control system, it works 7 days 24 hours without any intervention in the most appropriate way.
High efficiency rotor type heat exchanger Thermal efficiency up to 90%
Moisture transfer efficiency up to 65% Optional CO2 or pressure sensor
High efficiency EC Plug fans
50 mm thick double-walled panel construction
RTER Modal:Top and side switcable duct connection RTER-A Modal: Side duct connection



	Product Model
	RTER035

	Product Type
	Commercial Type Heat Recovery

	Heat Recovery Type
	Aluminum Rotary

	Unit Casing
	Double wall - Inside: 0.8 mm galvanized sheet

	Unit isolation
	50 mm 70 kg/m3-Rockwool

	Casing Air Leakage
	0

	Unit Frame
	-

	Service Direction
	Both Sides

	Voltage / Frequency / Phase (V / Hz / Ph)
	380/50/3

	Operating conditions
	-20 ~ 46 ° C Temperature, 90% Max.RH Outdoor Air

	Standard Air Density (kg/m³)
	1.2
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Dimensions


	L
	W
	H
	A
	B
	L1
	L2
	L3
	W(kg)

	1918
	1000
	1366
	315
	400
	893
	495
	530
	416



Performance Data

	Supply Air Flow
	m³/h
	3000
	Heat Recovery Efficiency
	%
	79.57

	External Static Pressure
	Pa
	200
	Heat Recovery Capacity
	kW
	16.09

	Return Air Flow
	m³/h
	3000
	Additional Heating Capacity
	kW
	0

	External Static Pressure
	Pa
	200
	Additional Cooling Capacity
	kW
	

	Unit Total Power / Current
	kW/A
	1.56/6.46
	Air Outlet Temperature
	°C
	20.91

	Supply Side Internal Pressure Loss
	Pa
	0
	Exhaust Side Internal Pressure Loss
	Pa
	0

	SFPint,total
	W/m³/s
	1096.44
	Energy Efficiency Class
	-
	




Heat Recovery Data

	Heat Recovery Type
	Aluminum Rotary - Enthalpy Rotor

	Fin Pitch (mm)
	1.6



	Winter
	
	Outside Air
	Return Air

	Air Inlet Flow
	m³/h
	3000
	3000

	Air Inlet Temperature (DB / WB)
	°C
	5 / 3
	25 / 14.04

	Air Inlet Relative Humidity
	%
	72
	28

	Air Outlet Temperature (DB / WB)
	°C
	20.91 / 11.13
	9.11 / 6.73

	Air Outlet Relative Humidity
	%
	27.77
	71.65

	Heat Recovery Pressure Drop
	Pa
	181.99
	205.29

	Heat Recovery Efficiency (Dry / Wet)
	%
	79.57 / 22.66
	-

	Heat Recovery Capacity (Sensible / Latent)
	kW
	16.09 / 0.91
	-16.08 / -0.91

	Heat Recovery Capacity (Total)
	kW
	17.00
	-16.99

	Condensation
	kg/h
	0.00
	0.00




	Summer
	
	Outside Air
	Return Air

	Air Inlet Flow
	m³/h
	3000
	3000

	Air Inlet Temperature (DB / WB)
	°C
	33 / 22.38
	22 / 13.89

	Air Inlet Relative Humidity
	%
	40
	40

	Air Outlet Temperature (DB / WB)
	°C
	24.31 / 18.77
	30.74 / 18.18

	Air Outlet Relative Humidity
	%
	59.38
	28.63

	Heat Recovery Pressure Drop
	Pa
	214.65
	201.80

	Heat Recovery Efficiency (Dry / Wet)
	%
	79.0379 / 21.95
	-

	Heat Recovery Capacity (Sensible / Latent)
	kW
	8.91 / 3.28
	8.92 / 3.28

	Heat Recovery Capacity (Total)
	kW
	12.18
	12.20

	Condensation
	kg/h
	0.00
	0.00




Filter Data

	
	
	SA Filter 1
	SA Filter 2
	EA Filter
	EA Filtre 2

	Filter Class
	-
	
	F7
	M5
	

	Filter Class (ISO 16890)
	-
	
	ISO ePM1 50%
	ISO ePM10 50%
	

	Filter Initial Pressure Drop
	Pa
	
	145.24
	125.24
	

	Filter Final Pressure Drop
	Pa
	
	200
	170
	

	Filter Average Pressure Drop
	Pa
	
	172.62
	147.62
	

	Filter Surface Air Velocity
	m/s
	
	4.1708
	4.1708
	4.1708



Fan Data

	
	
	Outside Air
	Return Air

	Air Flow
	m³/h
	3000
	3000

	Fan Speed
	d/d
	2055.7
	2032.03

	Nominal Fan Speed
	d/d
	2100
	2100

	Fan Power
	Watt
	732.34
	737

	Operating Point Current
	A
	3.22
	3.24

	Voltage / Frequency / Phase
	V/Hz/Ph
	230 / 50 / 1
	230 / 50 / 1




	Fan LWA
	
	
	LWA (In+Out)
	LWA
	63Hz
	125Hz
	250Hz
	500Hz
	1kHz
	2kHz
	4kHz
	8kHz

	
Supply Fan
	Inlet
	dBA
	
79,56
	73,17
	65,80
	69,40
	73,70
	72,20
	66,00
	64,20
	61,50
	54,20

	
	Outlet
	dBA
	
	78,36
	71,10
	74,80
	79,00
	77,40
	71,20
	69,40
	66,60
	59,50

	
Return Fan
	Inlet
	dBA
	
79,36
	73,17
	65,80
	69,40
	73,70
	72,20
	66,00
	64,20
	61,50
	54,20

	
	Outlet
	dBA
	
	78,36
	71,10
	74,80
	79,00
	77,40
	71,20
	69,40
	66,60
	59,50



	Fan LPA
	@ 1 m
	LPA (In+Out)
	LPA
	63Hz
	125Hz
	250Hz
	500Hz
	1kHz
	2kHz
	4kHz
	8kHz

	
Supply Fan
	Inlet
	dBA
	
71.58
	65.19
	57.82
	61.42
	65.72
	64.22
	58.02
	56.22
	53.52
	46.22

	
	Outlet
	dBA
	
	70.38
	63.12
	66.82
	71.02
	69.42
	63.22
	61.42
	58.62
	51.52

	
Return Fan
	Inlet
	dBA
	
71.58
	65.19
	57.82
	61.42
	65.72
	64.22
	58.02
	56.22
	53.52
	46.22

	
	Outlet
	dBA
	
	70.38
	63.12
	66.82
	71.02
	69.42
	63.22
	61.42
	58.62
	51.52
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